### Praesideo Call Station Module PRS-CSM

### Architects’ and Engineers’ Specifications

The call station module shall provide connections for microphone, loudspeaker, buzzer, switches and indicators to enable an installer to create custom build call station panels.

The call station based on this module shall have a network interface for fiber optical hybrid cabling with dual network connections, capable of redundant loop operation. The fiber optic network interface of this call station shall support multi-channel digital audio and control signals.

Its microphone input shall have a limiter and a speech filter to improve speech intelligibility and prevent clipping of the audio signal. The call station shall contain a digital audio processor with a 3-band fully parametric equalizer and semi parametric shelving equalizers for bass and treble control, sensitivity control and a supervision pilot tone generator and detector to monitor the internal signal paths.

It shall have a monitoring loudspeaker and headset connection with volume control. The chime and pre-recorded message parts of a call shall be audible via the connected loudspeaker or headset for monitoring by the operator.

It shall be possible to connect up to 16 call station keypads to the call station via a serial communication link. The call station shall provide the power supply for the keypads. The connected keypads shall provide various selection options for the call station.

The call station based on this module shall be remotely configurable via the network interface and it shall be powered from the network for easy installation or from an external (backup) power supply.

It shall provide two supervised control inputs to pass power supply status information, from e.g. a UPS, to the controller of the system, via the network.

It shall have a supervision system to monitor its functions and operation in compliancy to international standards. It shall have connection possibilities for LEDs, indicating network connectivity status, operation status and fault conditions. Fault conditions shall also be reported by the unit to a network connected system controller for logging purposes.

The call station based on this module shall support fail-safe operation, i.e. even if the controller of the audio system fails, the call station is still able to put through emergency calls to all audio outputs on the network.

The unit shall be able to operate at a maximum operating temperature of 55°C.

The call station shall be certified by an independent Notified Body for compliancy to the standards EN 60849, EN 54-16 and ISO 7240-16 for emergency sound systems.

The call station module shall be a Praesideo PRS-CSM, manufactured by Bosch Security Systems.