June 2017

| Americas Bosch Security Systems, Inc. 130 Perinton Parkway Fairport, New York, 14450, USA Phone: + 1 800 289 0096 Fax: +1 585 223 9180 security.sales@us.bosch.com www.boschsecurity.us | Europe, Middle East, Africa Bosch Security Systems B.V. P.O. Box 80002 5600 JB Eindhoven, The Netherlands Phone: + 31 40 2577 284 Fax: +31 40 2577 330 emea.securitysystems@bosch.com www.boschsecurity.com | Asia-Pacific Robert Bosch (SEA) Pte Ltd, Security Systems 11 Bishan Street 21 Singapore 573943 Phone: +65 6571 2600 Fax: +65 6571 2698 apr.securitysystems@bosch.com www.boschsecurity.com |
| --- | --- | --- |

Product Guide Specification

SECTION 28 23 19

DIGITAL VIDEO RECORDERS AND ANALOG RECORDING DEVICES

BOSCH DIVAR IP 7000 2U revision 2 IP VIDEO MANAGEMENT APPLIANCE

- – GENERAL

  - SUMMARY

    - Section Includes

      - Section 28 23 23 – Video Surveillance Systems Infrastructure

    - Related Sections

      - Section [28 23 13 – Video Surveillance Control and Management Systems]

      - Section [28 23 16 – Video Surveillance Monitoring and Supervisory Interfaces]

      - Section [28 23 23 – Video Surveillance Systems Infrastructure]

      - Section [28 23 29 – Video Surveillance Remote Devices]

**********Specifier’s note: Include those standards referenced elsewhere in this SECTION.

  - REFERENCES

    - European Norm (CE)

    - International Organization for Standardization (ISO)

      - 9001 – Quality System

  - DEFINITIONS

    - RAID: Redundant Array of Independent Disks is a technology that employs the simultaneous use of two or more hard disk drives to achieve greater levels of performance, reliability, and/or larger data volume sizes.

    - iSCSI: Internet SCSI is a protocol that allows clients (called initiators) to send SCSI commands to SCSI storage devices (targets) on remote servers via an IP network.

    - SNMP: Simple Network Management Protocol is a component of the Internet Protocol Suite as defined by the Internet Engineering Task Force (IETF). SNMP is used in network management systems to monitor network-attached devices for conditions that warrant administrative attention.

  - SYSTEM DESCRIPTION

    - Section Includes

      - Digital Video Recorders and Analog Recording Devices

    - Performance Requirements

      - The IP Video Management Appliance shall be a RAID-5 protected, all-in-one recording, viewing and management solution for network surveillance systems of up to 128 channels.

      - The IP Video Management Appliance shall include pre-installed and pre-licensed video management software and up to 64 TB (8 x 8 TB) storage capacity.

      - The IP Video Management Appliance shall offer a dual port Gigabit Ethernet network interface, 8 GB system memory and an Intel Xeon Quad Core Processor.

      - The IP Video Management Appliance shall offer remote health monitoring via a desktop application or a Web browser.

      - The IP Video Management Appliance shall offer remote video monitoring via a desktop application, Web browser, or iOS-based mobile device.

  - SUBMITTALS

    - Submit under provisions of Section [01 33 00.]

    - Product Data:

      - Manufacturer’s data, user and installation manuals for all equipment and software programs including computer equipment and other equipment required for complete video management system.

    - Shop Drawings; include

      - System device locations on architectural floor plans.

      - Full Schematic of system, including wiring information for all devices.

    - Closeout Submittals

      - User manual.

      - Parts list.

      - System device locations on architectural floor plans.

      - Wiring and connection diagram.

      - Maintenance requirements.

  - QUALITY ASSURANCE

    - Manufacturer:

      - Minimum of [10] years experience in manufacture and design Video Surveillance Devices.

    - Video Surveillance System:

      - This product shall be manufactured by a firm whose quality system is in compliance with the I.S. /ISO 9001/EN 29001, QUALITY SYSTEM.

    - Installer:

      - Minimum of [5] years experience installing Video Surveillance System.

  - DELIVERY, STORAGE AND HANDLING

    - Comply with requirements of Section 01 60 00.

    - Deliver materials in manufacture’s original, unopened, undamaged containers; and unharmed original identification labels.

    - Protect store materials from environmental and temperature conditions following manufacturer’s instructions.

    - Handle and operate products and systems according to manufacturer’s instructions.

    - Bosch provides off-the-shelf availability for our top selling products and same-day or 24-hour shipping.

  - WARRANTY

    - Provide manufacturer’s warranty covering 3 years for replacement and repair of defective equipment.

  - MAINTENANCE

    - Make ordering of new equipment for expansions, replacements, and spare parts available to dealers and end users.

    - Provide factory direct technical support from 8:00 a.m. to 8:00 p.m. via phone and e-mail.

- – PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturer:

[Bosch Security Systems, Inc.

130 Perinton Parkway

Fairport, New York, 1450, USA

Phone: + 1 800 289 0096

Fax: + 1 585 223 9180

security.sales@us.bosch.com

www.boschsecurity.us]

[Bosch Security Systems B.V.

P.O. Box 80002

5600 JB Eindhoven, The Netherlands

Phone: + 31 40 2577 284

Fax: +31 40 2577 330

emea.securitysystems@bosch.com

www.boschsecurity.com]

[Robert Bosch (SEA) Pte Ltd, Security Systems

11 Bishan Street 21

Singapore 573943

Phone: +65 6571 2600

Fax: +65 6571 2698

apr.securitysystems@bosch.com

www.boschsecurity.com]

    - Substitutions: [Not permitted.] [Under provisions of Division 1.]

      - [All proposed substitutions must be approved by the Architect or Engineer professional.]

      - [Proposed substitutions must provide a line-by-line compliance documentation.]

  - BOSCH DIVAR IP 7000 2U [DIP-7180-00N] [DIP-7183-4HD] [DIP-7183-8HD] [DIP-7184-4HD] [DIP-7184-8HD] [DIP-7186-8HD] [DIP-7188-8HD]

    - General Characteristics:

      - The IP Video Management Appliance shall be a RAID-5 protected, all-in-one recording, viewing and management solution for network surveillance systems of up to 128 channels.

      - The IP Video Management Appliance shall come with a pre-installed Bosch VMS license for connecting 32 concurrent recordable cameras.

      - The IP Video Storage Appliance shall offer an optional camera expansion license for 8 additional concurrent recordable cameras up to a maximum of 128 cameras per appliance.

      - Software updates shall be available free of charge during the product warranty period. The software installed on the IP Video Management Appliance shall not be subject to any additional Software Maintenance Agreements (SMAs).

      - The IP Video Management Appliance shall utilize “enterprise-rated” hard drives in a fault tolerant RAID-5 configuration.

      - The IP Video Management Appliance shall be a pre-configured and pre-installed video management solution with up to 64 TB (8 x 8 TB) of gross storage capacity.

      - The IP Video Management Appliance shall offer up to 52136 GB of net capacity storage.

      - The IP Video Management Appliance shall offer a bandwidth of 475 Mbit/s.

      - The IP Video Management Appliance shall offer a dual port Gigabit Ethernet network interface, 8 GB system memory and an Intel Xeon Quad Core Processor.

      - The IP Video Management Appliance shall offer remote monitoring via a desktop application or a Web browser.

    - Functions

      - The IP Video Management Appliance shall offer an energy-efficient hot-swap redundant power supply.

      - The IP Video Management Appliance shall offer hot-swap SATA-III hard drives providing up to 64 TB of gross storage capacity.

      - The IP Video Management Appliance shall come pre-installed and pre-configured with all necessary software.

      - The IP Video Management Appliance shall utilize Microsoft Windows Storage Server 2012 R2.

      - The Operating System of the IP Video Management Appliance shall run solid state disks in redundant configuration.

    - Access to Video

      - The IP Video Management Appliance shall deliver high-quality HD video despite low or limited bandwidth connections.

      - The IP Video Management Appliance shall offer Dynamic Transcoding technology that retrieves data and subsequently decodes and decompresses the data stream to a lower bit stream.

      - The IP Video Management Appliance shall instantly enhance the video detail to full HD quality when the video is paused.

    - Management

      - The IP Video Management Appliance shall come with the Bosch VMS management application pre-installed and pre-licensed.

      - The IP Video Management Appliance shall allow operators to use one central tool for configuration and operations management.

    - Health Monitoring

      - The IP Video Management Appliance shall provide SNMP, Remote Desktop and HTTP monitoring support.

      - The IP Video Management Appliance shall offer high-availability hardware, embedded design, and system wide monitoring.

    - Processor

      - The IP Video Management Appliance shall contain an Intel Xeon Processor E3-1275 V3 (8 MB Cache, 3.5 GHz) processor.

      - The IP Video Management Appliance processor shall contain one (1) socket.

      - The IP Video Management Appliance processor shall feature a 1 x 8 MB Level 2 cache memory.

      - The IP Video Management Appliance processor shall include ECC Unbuffered memory protection.

      - The IP Video Management Appliance processor shall contain a 1600 MHz maximum front side Bus.

    - Memory

      - The IP Video Management Appliance shall have 8 GB, DDR3-1666 ECC UNB (1 x 8 GB) of memory installed.

    - Storage

      - The IP Video Management Appliance shall contain up to eight (8) 3.5 in. SATA storage trays.

      - The IP Video Management Appliance shall have up to 8 x 8 TB SATA
(7,200 RPM, 64 MB cache, 3.5 in.) hard drives installed.

      - The IP Video Management Appliance shall offer a 3108-based SAS/SATA RAID card with 8 internal ports.

      - The IP Video Management Appliance shall include an AMD FirePro W4100; 4 x Mini Display Port graphics card.

      - The IP Video Management Appliance shall include a Creative Sound Blaster PCI sound card.

      - The IP Video Management Appliance shall include 2 x 120 GB SSD drives in RAID-1 configuration

    - Electrical:

      - [Input: 120 VAC

        - Actual Output Wattage from Power Supply: 4HD: 259.9 W, 8HD: 305.6 W

        - Efficiency of Power Supply: 92%

        - Total System Power Consumption: 4HD: 282.5 W, 8HD: 332.2 W

        - Total BTU/h: 4HD: 964.2, 8HD: 1133.9

        - Power Factor: .98

        - System AC Input VA Requirement: 4HD: 288.3 VA, 8HD: 339.0 VA]

      - [Input: 240 VAC

        - Actual Output Wattage from Power Supply: 4HD: 259.9 W, 8HD: 305.6 W

        - Efficiency of Power Supply: 94%

        - Total System Power Consumption: 4HD: 276.5 W, 8HD: 325.1 W

        - Total BTU/h: 4HD: 943.7, 8HD: 1109.7

        - Power Factor: .96

        - System AC Input VA Requirement: 4HD: 288.0 VA, 8HD: 338.7 VA]

    - Mechanical

      - Form Factor: 2 U Rack Mount

      - Power Supply: 740 W Platinum Level Redundant

      - USB Ports: Front: 2 USB 2.0 ports, Rear: 2 USB 2.0 ports, 2 USB 3.0 ports

      - Network: Dual Intel i210AT Gigabit LAN (teamed), 1 IPMI BMC port

      - Dimensions (H x W x D): 89 x 437 x 648 mm (3.5 x 17.2 x 25.5 in)

      - Weight: 23.6 kg (52 lb)

    - Environmental:

      - Operating Temperature: +10°C to +35°C (+50°F to +95°F)

      - Non-operating Temperature: –40°C to +70°C (–40°F to +158°F)

      - Operating Relative Humidity: 8 to 90%, non-condensing

      - Non-operating Relative Humidity: 5 to 95%, non-condensing

    - Accessories:

      - DIP-6703-HDD: 3TB SATA Hard Drive

      - DIP-6704-HDD: 4TB SATA Hard Drive

      - DIP-6706-HDD: 6TB SATA Hard Drive

      - DIP-6708-HDD: 8TB SATA Hard Drive

    - Software Options

      - MBV-BXPAN-DIP DIVAR IP Professional Edition, Base expansion, 128 channels max

      - MBV-XCHAN-DIP DIVAR IP 8-Channel Expansion

      - MBV-XWST-DIP DIVAR IP Workstation Expansion

      - MBV-XDVR-DIP DIVAR IP DVR Expansion

      - MBV-XKBD-DIP DIVAR IP CCTV Keyboard Expansion

      - MBV-XMVS-DIP DIVAR IP Mobile Video Service Expansion

      - MBV-FALG-DIP DIVAR IP Allegiant Matrix Connection

      - MBV-FOPC-DIP DIVAR IP OPC Server Connection

      - MBV-XINT-DIP DIVAR IP Intrusion Panel Expansion

- – EXECUTION

  - EXAMINATION

    - Examine areas to receive devices and notify adverse conditions affecting installation or subsequent operation.

    - Do not begin installation until unacceptable conditions are corrected.

  - PREPARATION

    - Protect devices from damage during construction.

  - INSTALLATION

    - Install devices in accordance with manufacturer’s instruction at locations indicated on the floor drawings plans.

    - Perform installation with qualified service personnel.

    - Install devices in accordance with the National Electrical Code or applicable local codes.

    - Ensure selected location is secure and offers protection from accidental damage.

    - Location must provide reasonable temperature and humidity conditions, free from sources of electrical and electromagnetic interference.

  - FIELD QUALITY CONTROL

    - Test snugness of mounting screws of all installed equipment.

    - Test proper operation of all video system devices.

    - Determine and report all problems to the manufacturer’s customer service department.

  - ADJUSTING

    - Make proper adjustment to video system devices for correct operation in accordance with manufacturer’s instructions.

    - Make any adjustment of camera settings to comply with specific customer’s need.

  - DEMONSTRATION

    - Demonstrate at final inspection that video management system and devices functions properly.

END OF SECTION

# Text boxes

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, based on MasterFormat 2004 and The Project Resource Manual—CSI Manual of Practice. The Manufacturer is responsible for technical accuracy.

The section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Words and sentences within brackets [ ] are choices to include or exclude a particular item or statement.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” after editing this section.